## Table 1
Polyethylene (PE) SDR 7, 9, 11.5, 15 | [8 empty] | PVC Schedule 80 IPS
Sizes 1" through 2" Flow 1 gpm through 100 gpm | [8 empty] | Sizes 1" through 2" Flow 1 gpm through 100 gpm
Friction loss per 100 Feet of Pipe (psi/100 ft.) | [8 empty] | Friction loss per 100 Feet of Pipe (psi/100 ft.)
Nominal Size Avg. I.D. | 1" 1.049 |  | 1 1/4" 1.380 |  | 1 1/2" 1.610 |  | 2" 2.067 |  | Nominal Size Avg. I.D. | 1" 0.935 |  | 1 1/4" 1.254 |  | 1 1/2" 1.476 |  | 2" 1.913
Flow (gpm) | Velocity (ft/s) | Loss (psi) | Velocity (ft/s) | Loss (psi) | Velocity (ft/s) | Loss (psi) | Velocity (ft/s) | Loss (psi) | Flow (gpm) | Velocity (ft/s) | Loss (psi) | Velocity (ft/s) | Loss (psi) | Velocity (ft/s) | Loss (psi) | Velocity (ft/s) | Loss (psi)
1 | 0.37 | 0.04 | 0.21 | 0.01 | 0.16 | 0 | 0.1 | 0 | 1 | 0.47 | 0.06 | 0.26 | 0.01 | 0.19 | 0.01 | 0.11 | 0
2 | 0.74 | 0.14 | 0.43 | 0.04 | 0.31 | 0.02 | 0.19 | 0.01 | 2 | 0.93 | 0.21 | 0.52 | 0.05 | 0.37 | 0.02 | 0.22 | 0.01
3 | 1.11 | 0.29 | 0.64 | 0.08 | 0.47 | 0.04 | 0.29 | 0.01 | 3 | 1.4 | 0.45 | 0.78 | 0.11 | 0.56 | 0.05 | 0.33 | 0.01
4 | 1.48 | 0.5 | 0.86 | 0.13 | 0.63 | 0.06 | 0.38 | 0.02 | 4 | 1.87 | 0.77 | 1.04 | 0.18 | 0.75 | 0.08 | 0.45 | 0.02
5 | 1.85 | 0.76 | 1.07 | 0.2 | 0.79 | 0.09 | 0.48 | 0.03 | 5 | 2.33 | 1.16 | 1.3 | 0.28 | 0.94 | 0.13 | 0.56 | 0.04
6 | 2.22 | 1.06 | 1.29 | 0.28 | 0.94 | 0.13 | 0.57 | 0.04 | 6 | 2.8 | 1.63 | 1.56 | 0.39 | 1.12 | 0.18 | 0.67 | 0.05
7 | 2.6 | 1.41 | 1.5 | 0.37 | 1.1 | 0.18 | 0.67 | 0.05 | 7 | 3.27 | 2.17 | 1.82 | 0.52 | 1.31 | 0.24 | 0.78 | 0.07
8 | 2.97 | 1.8 | 1.71 | 0.47 | 1.26 | 0.22 | 0.76 | 0.07 | 8 | 3.73 | 2.78 | 2.08 | 0.67 | 1.5 | 0.3 | 0.89 | 0.09
9 | 3.34 | 2.24 | 1.93 | 0.59 | 1.42 | 0.28 | 0.86 | 0.08 | 9 | 4.2 | 3.45 | 2.34 | 0.83 | 1.69 | 0.37 | 1 | 0.11
10 | 3.71 | 2.73 | 2.14 | 0.72 | 1.57 | 0.34 | 0.95 | 0.1 | 10 | 4.67 | 4.2 | 2.59 | 1.01 | 1.87 | 0.46 | 1.11 | 0.13
11 | 4.08 | 3.25 | 2.36 | 0.86 | 1.73 | 0.4 | 1.05 | 0.12 | 11 | 5.13 | 5.01 | 2.85 | 1.2 | 2.06 | 0.54 | 1.23 | 0.15
12 | 4.45 | 3.82 | 2.57 | 1.01 | 1.89 | 0.48 | 1.15 | 0.14 | 12 | 5.6 | 5.88 | 3.11 | 1.41 | 2.25 | 0.64 | 1.34 | 0.18
14 | 5.19 | 5.08 | 3 | 1.34 | 2.2 | 0.63 | 1.34 | 0.19 | 14 | 6.53 | 7.83 | 3.63 | 1.88 | 2.62 | 0.85 | 1.56 | 0.24
16 | 5.93 | 6.51 | 3.43 | 1.71 | 2.52 | 0.81 | 1.53 | 0.24 | 16 | 7.47 | 10.03 | 4.15 | 2.4 | 3 | 1.09 | 1.78 | 0.31
18 | 6.67 | 8.1 | 3.86 | 2.13 | 2.83 | 1.01 | 1.72 | 0.3 | 18 | 8.4 | 12.47 | 4.67 | 2.99 | 3.37 | 1.35 | 2.01 | 0.38
20 | 7.42 | 9.84 | 4.28 | 2.59 | 3.15 | 1.22 | 1.91 | 0.36 | 20 | 9.33 | 15.16 | 5.19 | 3.63 | 3.75 | 1.64 | 2.23 | 0.47
22 | 8.16 | 11.74 | 4.71 | 3.09 | 3.46 | 1.46 | 2.1 | 0.43 | 22 | 10.27 | 18.08 | 5.71 | 4.33 | 4.12 | 1.96 | 2.45 | 0.56
24 | 8.9 | 13.79 | 5.14 | 3.63 | 3.78 | 1.72 | 2.29 | 0.51 | 24 | 11.2 | 21.24 | 6.23 | 5.09 | 4.49 | 2.3 | 2.68 | 0.65
26 | 9.64 | 16 | 5.57 | 4.21 | 4.09 | 1.99 | 2.48 | 0.59 | 26 | 12.13 | 24.64 | 6.75 | 5.91 | 4.87 | 2.67 | 2.9 | 0.76
28 | 10.38 | 18.35 | 6 | 4.83 | 4.41 | 2.28 | 2.67 | 0.68 | 28 | 13.07 | 28.26 | 7.26 | 6.77 | 5.24 | 3.06 | 3.12 | 0.87
30 | 11.12 | 20.85 | 6.43 | 5.49 | 4.72 | 2.59 | 2.86 | 0.77 | 30 | 14 | 32.12 | 7.78 | 7.7 | 5.62 | 3.48 | 3.34 | 0.99
35 | 12.98 | 27.74 | 7.5 | 7.3 | 5.51 | 3.45 | 3.34 | 1.02 | 35 | 16.33 | 42.73 | 9.08 | 10.24 | 6.55 | 4.63 | 3.9 | 1.31
40 |  |  | 8.57 | 9.35 | 6.3 | 4.42 | 3.82 | 1.31 | 40 |  |  | 10.38 | 13.11 | 7.49 | 5.93 | 4.46 | 1.68
45 |  |  | 9.64 | 11.63 | 7.08 | 5.49 | 4.3 | 1.63 | 45 |  |  | 11.68 | 16.31 | 8.43 | 7.38 | 5.02 | 2.09
50 |  |  | 10.71 | 14.14 | 7.87 | 6.68 | 4.77 | 1.98 | 50 |  |  | 12.97 | 19.83 | 9.36 | 8.97 | 5.57 | 2.54
55 |  |  | 11.78 | 16.87 | 8.66 | 7.97 | 5.25 | 2.36 | 55 |  |  | 14.27 | 23.65 | 10.3 | 10.7 | 6.13 | 3.03
60 |  |  | 12.85 | 19.82 | 9.44 | 9.36 | 5.73 | 2.77 | 60 |  |  | 15.57 | 27.79 | 11.24 | 12.57 | 6.69 | 3.56
65 |  |  |  |  | 10.23 | 10.86 | 6.21 | 3.22 | 65 |  |  |  |  | 12.17 | 14.58 | 7.25 | 4.13
70 |  |  |  |  | 11.02 | 12.45 | 6.68 | 3.69 | 70 |  |  |  |  | 13.11 | 16.73 | 7.8 | 4.74
75 |  |  |  |  | 11.81 | 14.15 | 7.16 | 4.19 | 75 |  |  |  |  | 14.05 | 19.01 | 8.36 | 5.38
80 |  |  |  |  | 12.59 | 15.95 | 7.64 | 4.73 | 80 |  |  |  |  | 14.98 | 21.42 | 8.92 | 6.06
85 |  |  |  |  | 13.38 | 17.84 | 8.12 | 5.29 | 85 |  |  |  |  | 15.92 | 23.96 | 9.48 | 6.78
90 | [6 empty] | 8.59 | 5.88 | 90 | [6 empty] | 10.03 | 7.54
95 | [6 empty] | 9.07 | 6.5 | 95 | [6 empty] | 10.59 | 8.34
100 | [6 empty] | 9.55 | 7.15 | 100 | [6 empty] | 11.15 | 9.17